Cube Humidity Controller - Documentation

Leaf Controller

[24th February 2021]

Document Control Number:

Revision Number: 0.1

Expiration Date:

Author: Kai Weber

Approval: ____________________________________

Revision History

| Date | Revision Number | Pages Affected |
| --- | --- | --- |
| 20th February 2021 | 0.1 | Initial release |

Table of Contents

1.	Using the Modbus Script	2

2.	Functionality	2

2.1	Table of actions	3

2.2	SW Control Logic	4

3.	Implementation	5

# Using the Modbus Script

The script should be located in the directory /usr/local/bin on the banana pi. It can be started with the following command:

fluence_controller.py

The script implements the functionality, as described in the PowerPoint presentation “Cube humidity control”.

# Functionality

The following table of actions and flowchart from the PowerPoint presentation “Cube humidity control”, describe the functionality.

## Table of actions

| Condition #1 [Tair] | Condition #2 [RH limit exceeded] | Set-point | Action until |
| --- | --- | --- | --- |
| Tair < 15°C | N/A | 15°C | Heat until Tair = SP |
| 15°C < Tair < 18°C | RH > 85% | 15°C | [Cool until Tair = SP] OR [max 1h] OR [RH – 10%] (*) |
| 18°C < Tair < 21°C | RH > 75% | 17°C | [Cool until Tair = SP] OR [max 1h] OR [RH – 10%] (*) |
| 21°C < Tair < 24°C | RH > 62% | 20°C | [Cool until Tair = SP] OR [max 1h] OR [RH – 10%] (*) |
| 24°C < Tair < 27°C | RH > 53% | 23°C | [Cool until Tair = SP] OR [max 1h] OR [RH – 10%] (*) |
| 27°C < Tair < 30°C | RH > 45% | 25°C | [Cool until Tair = SP] (**) |
| T > 30°C | RH > 40% | 25°C | [Cool until Tair = SP] (**) |

## SW Control Logic

# Implementation

The script will initialize itself, by reading the configuration from the same config file, that is also used by the script controllino_modbus.py.

By reading the config file, the script will know if it is running in a Cube or OCTE and furthermore if one or two HVACs are connected to the Cube Controller.

After the initialization, the main functionality is implemented in a while-true loop with the following steps:

- Derive temperature, humidity and dl10 read alarm from dl10 sensor

- Check if values of dl10 are valid and dl10 read alarm status

  - The values are valid, and the read alarm is false

    - Calculate the setpoint for the HVACs depending on the temperature, humidity and the time elapsed since the current setpoint has been set

    - Write the new setpoint to the HVACs.

    - Sleep for ten seconds.

    - Return to step 1.

  - The values are invalid, or the read alarm is true

    - Write emergency value for refrigeration stop point of 20°C to the HVACs.

    - Sleep for ten seconds.

    - Return to step 1.