## LD Cube
xid | name | textRenderer/type | pointLocator/slaveId | pointLocator/range | pointLocator/modbusDataType | pointLocator/offset | pointLocator/multiplier | pointLocator/bit | textRenderer/suffix | pointLocator/writeType | Enabled | textRenderer/oneLabel | textRenderer/zeroLabel | textRenderer/format | readPermission | setPermission | tags/deviceFunction | tags/pointMeasure | tags/alarmLow | tags/warningLow | tags/warningHigh | tags/alarmHigh | tags/hmiDisplay | Note | Tested
| Door Contact 1 | BINARY | 42 | INPUT_REGISTER | BINARY | 0 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| Door Contact 2 | BINARY | 42 | INPUT_REGISTER | BINARY | 1 | 1 | 0 |  | NOT_SETTABLE | FALSE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| reserve | BINARY | 42 | INPUT_REGISTER | BINARY | 2 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| Core IMD (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 3 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| F-Stop button (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 4 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| BMS F-Stop(OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 5 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| Pre-fire panel signal point (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 6 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| Main F-Stop relay (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 7 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| F-Stop K1 (CUBE) | BINARY | 42 | INPUT_REGISTER | BINARY | 8 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| F-Stop push button (CUBE) | BINARY | 42 | INPUT_REGISTER | BINARY | 9 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| Leakage sensor | BINARY | 42 | INPUT_REGISTER | BINARY | 10 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| 24V Power supply | BINARY | 42 | INPUT_REGISTER | BINARY | 11 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| SPF (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 12 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| UPS (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 13 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| HVAC (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 14 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| MV Transformer pressure (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 15 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| MV Transformer oil level (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 16 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| MV Transformer oil temperature (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 17 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| MV Transformer winding temperature (OCTE) | BINARY | 42 | INPUT_REGISTER | BINARY | 18 | 1 | 0 |  | NOT_SETTABLE | TRUE | NORMAL | ALARM | #,##0 | full-access,read-only,owner | full-access | bop | ALARM |  |  |  | 1 | TRUE
| Temp sensor 1 | ANALOG | 42 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 19 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access | bop | Analog
| Temp sensor 2 | ANALOG | 42 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 20 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access | bop | Analog
| Temp sensor 3 | ANALOG | 42 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 21 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access | bop | Analog
| Temp sensor 4 | ANALOG | 42 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 22 | 0.1 | 0 | Deg C | NOT_SETTABLE | FALSE |  |  | #,##0.0 | full-access,read-only,owner | full-access | bop | Analog
| Temp sensor 5 | ANALOG | 42 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 23 | 0.1 | 0 | Deg C | NOT_SETTABLE | FALSE |  |  | #,##0.0 | full-access,read-only,owner | full-access | bop | Analog
| Temp sensor 6 | ANALOG | 42 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 24 | 0.1 | 0 | Deg C | NOT_SETTABLE | FALSE |  |  | #,##0.0 | full-access,read-only,owner | full-access | bop | Analog
| Cube heartbeat counter | ANALOG | 42 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 25 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | read-only,full-access | full-access |  | Analog
| HVAC 01 Unit running status | BINARY | 3 | HOLDING_REGISTER | BINARY | 256 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Internal fan status | BINARY | 3 | HOLDING_REGISTER | BINARY | 257 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 External fan status | BINARY | 3 | HOLDING_REGISTER | BINARY | 258 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Compressor status | BINARY | 3 | HOLDING_REGISTER | BINARY | 259 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Heater status | BINARY | 3 | HOLDING_REGISTER | BINARY | 260 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Emergency fan status | BINARY | 3 | HOLDING_REGISTER | BINARY | 261 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Evaporator Temp. | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1280 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| HVAC 01 Outdoor Temp. | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1281 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| HVAC 01 Condenser Temp. | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1282 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| HVAC 01 Indoor Temp. | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1283 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| HVAC 01 Humidity | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1284 | 0.1 | 0 | % | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| HVAC 01 Discharge Temp. | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1285 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| HVAC 01 AC running current | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1286 | 0.001 | 0 | A | NOT_SETTABLE | TRUE |  |  | #,##0.000 | full-access,read-only,owner | full-access
| HVAC 01 AC input voltage | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1287 | 1 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| HVAC 01 DC input voltage | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1288 | 0.1 | 0 | V | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| HVAC 01 High Temp. alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1536 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Low Temp. alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1537 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 High humidity alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1538 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Low humidity alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1539 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Coil freeze protection | BINARY | 3 | HOLDING_REGISTER | BINARY | 1540 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 High exhaust Temp. alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1541 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Evaporator Temp. sensor failure | BINARY | 3 | HOLDING_REGISTER | BINARY | 1542 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Outdoor Temp. sensor failure | BINARY | 3 | HOLDING_REGISTER | BINARY | 1543 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Condenser Temp. sensor failure | BINARY | 3 | HOLDING_REGISTER | BINARY | 1544 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Indoor Temp. sensor failure | BINARY | 3 | HOLDING_REGISTER | BINARY | 1545 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Exhaust Temp. sensor failure | BINARY | 3 | HOLDING_REGISTER | BINARY | 1546 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Humidity sensor failure | BINARY | 3 | HOLDING_REGISTER | BINARY | 1547 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Internal fan failure alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1548 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 External fan failure alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1549 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Compressor failure alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1550 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Heater failure alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1551 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Emergency fan failure alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1552 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 HP. alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1553 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 LP. alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1554 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Water alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1555 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Fire alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1556 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Gating alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1557 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 HP. lock | BINARY | 3 | HOLDING_REGISTER | BINARY | 1558 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 LP. lock | BINARY | 3 | HOLDING_REGISTER | BINARY | 1559 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 High exhaust Temp. lock | BINARY | 3 | HOLDING_REGISTER | BINARY | 1560 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 AC over voltage alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1561 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 AC under voltage alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1562 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 AC power supply failure | BINARY | 3 | HOLDING_REGISTER | BINARY | 1563 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Lose phase alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1564 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Freq.fault | BINARY | 3 | HOLDING_REGISTER | BINARY | 1565 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Anti phase alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1566 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 DC over voltage alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1567 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 DC under voltage alarm | BINARY | 3 | HOLDING_REGISTER | BINARY | 1568 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access |  | ALARM
| HVAC 01 Refrigeration stop point | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1792 | 1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| HVAC 01 Refrigeration band | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1793 | 1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| HVAC 01 Heating stop point | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1794 | 1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| HVAC 01 Heating band | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1795 | 1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| HVAC 01 High Temp.point | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1798 | 1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| HVAC 01 Low Temp. point | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1799 | 1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| HVAC 01 High humidity point | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1800 | 1 | 0 | % | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| HVAC 01 Internal fan stop point | ANALOG | 3 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1801 | 1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| HVAC 01 Remote control | BINARY | 3 | HOLDING_REGISTER | BiNARY | 2049 | 1 | 0 |  | SETTABLE | TRUE | ON | OFF | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 System ON/OFF | BINARY | 1 | HOLDING_REGISTER | BINARY | 1024 | 1 | 0 |  | SETTABLE | TRUE | ON | OFF | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Mode selection | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1025 | 1 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Water temperature setting | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 35596 | 0.1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Heating setpoint | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 35597 | 0.1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Hysteresis setting | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 35598 | 0.1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Hysteresis heating setting | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 35599 | 0.1 | 0 | Deg C | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Flow rate selection | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 38921 | 1 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Supply water temperature | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 40960 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Return water temperature | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 40962 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Environment temperature | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 40973 | 0.1 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Inlet water pressure | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 40974 | 0.01 | 0 | Bar | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Outlet water pressure | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 40975 | 0.01 | 0 | Bar | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Outlet high water temperature | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45312 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Outlet low water temperature | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45313 | 1 | 0 |  | NOT_SETTABLE | TRUE | ALARM | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Outlet water temperature sensor failure | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45314 | 1 | 0 |  | NOT_SETTABLE | TRUE | FAULT | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Return water temperature sensor failure | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45316 | 1 | 0 |  | NOT_SETTABLE | TRUE | FAULT | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Heating failure | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45323 | 1 | 0 |  | NOT_SETTABLE | TRUE | FAULT | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Pump failure | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45329 | 1 | 0 |  | NOT_SETTABLE | TRUE | FAULT | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Inverter communication failure | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45333 | 1 | 0 |  | NOT_SETTABLE | TRUE | FAULT | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 High system pressure alarm | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45340 | 1 | 0 |  | NOT_SETTABLE | TRUE | FAULT | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 High outlet pressure alarm | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45360 | 1 | 0 |  | NOT_SETTABLE | TRUE | FAULT | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Water replenishment alarm | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45362 | 1 | 0 |  | NOT_SETTABLE | TRUE | LACK OF FLUID | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 System high voltage lock | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45367 | 1 | 0 |  | NOT_SETTABLE | TRUE | LOCK | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 System low voltage lock | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45368 | 1 | 0 |  | NOT_SETTABLE | TRUE | LOCK | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Exhaust gas high temperature lock | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45369 | 1 | 0 |  | NOT_SETTABLE | TRUE | LOCK | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Inverter overcurrent lock | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45370 | 1 | 0 |  | NOT_SETTABLE | TRUE | LOCK | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Inverter over temperature lock | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45371 | 1 | 0 |  | NOT_SETTABLE | TRUE | LOCK | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Inverter overvoltage lock | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45372 | 1 | 0 |  | NOT_SETTABLE | TRUE | LOCK | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Inverter undervoltage lock | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45373 | 1 | 0 |  | NOT_SETTABLE | TRUE | LOCK | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Inverter phase loss lock | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45374 | 1 | 0 |  | NOT_SETTABLE | TRUE | LOCK | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Inverter other fault lock | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45375 | 1 | 0 |  | NOT_SETTABLE | TRUE | LOCK | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Heating fault lock | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45378 | 1 | 0 |  | NOT_SETTABLE | TRUE | LOCK | NORMAL | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Pump command speed | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 41473 | 0.1 | 0 | % | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Heartbeat | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 32772 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Password | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 33024 | 1 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Compressor gear select | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 35112 | 1 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Compressor speed select | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 35082 | 1 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Baudrate | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 35337 | 1 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 ID | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 36864 | 1 | 0 |  | SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Software part no | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 65105 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| Chiller 01 Software version no | ANALOG | 1 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 65106 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| DL10 Humidity | ANALOG | 5 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 0 | 0.01 | 0 | % | NOT_SETTABLE | TRUE |  |  | #,##0.00 | full-access,read-only,owner | full-access |  | Analog
| DL10 Temp sensor in °C | ANALOG | 5 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 1 | 0.01 | 0 | Deg C | NOT_SETTABLE | TRUE |  |  | #,##0.00 | full-access,read-only,owner | full-access |  | Analog
| DL10 Temp sensor in °F | ANALOG | 5 | INPUT_REGISTER | TWO_BYTE_INT_SIGNED | 2 | 0.01 | 0 | Deg F | NOT_SETTABLE | TRUE |  |  | #,##0.00 | full-access,read-only,owner | full-access |  | Analog
| UPS battery capacity | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 0 | 0.1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| UPS battery charge | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 1 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS battery charge low | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 2 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS battery charge restart | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 3 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS battery charger status | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 4 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS battery energysave | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 5 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS battery energysave delay | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 6 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS battery energysave load | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 7 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS battery protection | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 8 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS battery runtime | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 9 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS battery type | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 10 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS battery voltage | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 11 | 0.1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| UPS battery voltage nominal | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 12 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS device mfr | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 13 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS device model | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 14 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS device serial | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 15 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS device type | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 16 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS driver name | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 17 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS driver parameter pollfreq | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 18 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS driver parameter pollinterval | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 19 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS driver parameter port | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 20 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS driver parameter synchronous | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 21 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS driver version | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 22 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS driver version data | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 23 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS driver version internal | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 24 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS input current | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 25 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS input frequency | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 26 | 0.1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| UPS input frequency extended | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 27 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS input frequency nominal | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 28 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS input sensitivity | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 29 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS input transfer boost low | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 30 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS input transfer high | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 31 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS input transfer low | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 32 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS input transfer trim high | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 33 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS input voltage | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 34 | 0.1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| UPS input voltage extended | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 35 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS input voltage nominal | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 36 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 1 autoswitch charge low | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 37 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 1 delay shutdown | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 38 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 1 delay start | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 39 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 1 desc | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 40 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 1 id | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 41 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 1 status | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 42 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 1 switchable | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 43 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 2 autoswitch charge low | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 44 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 2 delay shutdown | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 45 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 2 delay start | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 46 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 2 desc | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 47 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 2 id | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 48 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 2 status | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 49 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet 2 switchable | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 50 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet desc | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 51 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet id | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 52 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS outlet switchable | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 53 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS output current | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 54 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS output frequency | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 55 | 0.1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| UPS output frequency nominal | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 56 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS output powerfactor | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 57 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS output voltage | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 58 | 0.1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0.0 | full-access,read-only,owner | full-access
| UPS output voltage nominal | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 59 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups beeper status | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 60 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups delay shutdown | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 61 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups delay start | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 62 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups efficiency | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 63 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups firmware | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 64 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups load | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 65 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups load high | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 66 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups mfr | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 67 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups model | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 68 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups power | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 69 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups power nominal | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 70 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups productid | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 71 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups realpower | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 72 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups realpower nominal | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 73 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups serial | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 74 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups shutdown | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 75 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups start auto | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 76 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups start battery | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 77 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups start reboot | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 78 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups status | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 79 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups test interval | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 80 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups test result | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 81 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups timer shutdown | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 82 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups timer start | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 83 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups type | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 84 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access
| UPS ups vendorid | ANALOG | 21 | HOLDING_REGISTER | TWO_BYTE_INT_SIGNED | 85 | 1 | 0 |  | NOT_SETTABLE | TRUE |  |  | #,##0 | full-access,read-only,owner | full-access

## Sheet1
UPS | battery capacity
UPS | battery charge
UPS | battery charge low
UPS | battery charge restart
UPS | battery charger status
UPS | battery energysave
UPS | battery energysave delay
UPS | battery energysave load
UPS | battery protection
UPS | battery runtime
UPS | battery type
UPS | battery voltage
UPS | battery voltage nominal
UPS | device mfr
UPS | device model
UPS | device serial
UPS | device type
UPS | driver name
UPS | driver parameter pollfreq
UPS | driver parameter pollinterval
UPS | driver parameter port
UPS | driver parameter synchronous
UPS | driver version
UPS | driver version data
UPS | driver version internal
UPS | input current
UPS | input frequency
UPS | input frequency extended
UPS | input frequency nominal
UPS | input sensitivity
UPS | input transfer boost low
UPS | input transfer high
UPS | input transfer low
UPS | input transfer trim high
UPS | input voltage
UPS | input voltage extended
UPS | input voltage nominal
UPS | outlet 1 autoswitch charge low
UPS | outlet 1 delay shutdown
UPS | outlet 1 delay start
UPS | outlet 1 desc
UPS | outlet 1 id
UPS | outlet 1 status
UPS | outlet 1 switchable
UPS | outlet 2 autoswitch charge low
UPS | outlet 2 delay shutdown
UPS | outlet 2 delay start
UPS | outlet 2 desc
UPS | outlet 2 id
UPS | outlet 2 status
UPS | outlet 2 switchable
UPS | outlet desc
UPS | outlet id
UPS | outlet switchable
UPS | output current
UPS | output frequency
UPS | output frequency nominal
UPS | output powerfactor
UPS | output voltage
UPS | output voltage nominal
UPS | ups beeper status
UPS | ups delay shutdown
UPS | ups delay start
UPS | ups efficiency
UPS | ups firmware
UPS | ups load
UPS | ups load high
UPS | ups mfr
UPS | ups model
UPS | ups power
UPS | ups power nominal
UPS | ups productid
UPS | ups realpower
UPS | ups realpower nominal
UPS | ups serial
UPS | ups shutdown
UPS | ups start auto
UPS | ups start battery
UPS | ups start reboot
UPS | ups status
UPS | ups test interval
UPS | ups test result
UPS | ups timer shutdown
UPS | ups timer start
UPS | ups type
UPS | ups vendorid